## Pathway Fill Calculators
Welcome to Leviton's Pathway Fill Calculator
To calculate conduit fill ratios for copper, fiber, and Industrial Ethernet products, please use the For Conduit calcutor.
To calculate basket tray fill ratios for copper, fiber, and Industrial Ethernet products, please use the For Basket Tray calcutor.
Version 2024-07-08
IMPORTANT NOTICE: This calculator is provided for informational purposes only in order to illustrate typical product constructions, applications, and/or methods of installation. Because conditions of actual installation and use are unique and will vary, Leviton makes no representation or warranty as to the reliability, accuracy or completeness of this data, even if Leviton is aware of the product's intended use or purpose. Furthermore, this data does not constitute, nor should it be regarded or relied upon, as professional engineering advice. Installation of product should only be done by qualified personnel and in conformance with all safety, electrical and other applicable codes, standards, rules or regulations. Appropriate and correct product selection, installation and use, and compliance with all such codes, standards, rules and regulations, is a customer/end­user responsibility. Product specifications, standards, programs, software, or services are subject to improvement or changes without notice. Leviton accepts no liability for typographical errors, technical inaccuracies, omissions or misuse of the information contained herein. Changes will be periodically made to address any such issues.
Accurately calculate conduit fills using the simple tool below.
FOR CONDUIT Step 1) Select your Conduit from the drop list at right. | Conduit/Duct I.D. inch | I.D. (inches) | Conduit Internal Area
| EMT 3/8 | 0.493 | 0.19089
Step 2) Select your cable category and type from the drop down lists at right. If installing multiple cable types in a single conduit, use a separate row for each. The O.D. Column will automatically populate and calculate the cross-sectional area for each cable.
| Cable Category | Cable Type | O.D. | Area | Number of Cables | Areasum | Hyperlink
| Select Category | Select Category First | 0 | 0 |  | 0
| Select Category | Select Category First | 0 | 0 |  | 0
| Select Category | Select Category First | 0 | 0 |  | 0
| Select Category | Select Category First | 0 | 0 |  | 0
Step 3) Enter the number of cables planned to be installed in each conduit. | Select Category | Select Category First | 0 | 0 |  | 0
| Select Category | Select Category First | 0 | 0 |  | 0
| User-Specified OD |  |  | 0 |  | 0
0
Step 4) Compare the Fill Ratio Value against the NFPA 70 fill limits shown in green. If the value in K38 is larger than the allowable fill ratio (by cable count), then the cell will be highlighted in red. If it is highlighted in green, the proposed installation is compliant to NFPA 70 recommended fill limits.
[6 empty] | 0% | 0% | Max Fill: | 0
Fill Ratio
Backbone Cable Conduit Fill Limits
|  | 1 Cable | 53% | Values drawn from NFPA 70, NEC (National Electrical Code), Chapter 9, Table 1 |  |  | Fill ratio is good!
|  | 2 Cables | 31% |  |  |  | Above the allowable fill ratio
|  | > 2 Cables | 40%
An error exists
Accurately calculate basket tray fills using the simple tool below.
FOR BASKET TRAY Step 1) Enter the basket tray width & height in inches. | Basket Tray Width (inches) | Basket Tray Height (inches) | Basket Tray Area (sq. in.)
| 3 | 4 | 12
Step 2) Select your cable category and type from the drop down lists at right. If installing multiple cable types in a single basket tray, use a separate row for each. The O.D. Column will automatically populate and calculate the cross-sectional area for each cable.
| Cable Category | Cable Type | O.D. | Area | Number of Cables | Areasum | Hyperlink
| Select Category | Select Category First | 0 | 0 |  | 0
| Select Category | Select Category First | 0 | 0 |  | 0
| Select Category | Select Category First | 0 | 0 |  | 0
| Select Category | Select Category First | 0 | 0 |  | 0
| Select Category | Select Category First | 0 | 0 |  | 0
Step 3) Enter the number of cables planned to be installed in each tray. | Select Category | Select Category First | 0 | 0 |  | 0
| User-Specified OD |  |  | 0 |  | 0
[6 empty] | 0 |  | Green: | 0
[8 empty] | Yellow: | 0
Step 4) Compare the Fill Ratio Value against the fill ration standards below. If the value in K67 is larger than the recommended fill ratio, then the cell will be highlighted in red. If it is between 40% and 50%, it will be highlighted in gold and it will be highlighted in green if it is at 40% or lower fill ratio. | [5 empty] | 0% | 0%
Fill Ratio
Fill Ratio Standards Your fill ratio is highlighted in the box at right. Per TIA 569, max calculated fill ratio is 50%. Due to the random way cables are laid into a tray, 50% fill actually fills the cable tray to 100%. 40% calculated fill is recommended for future expansion and additions into the tray. If your fill ratio exceeds 40% you should consider using a larger cable tray to allow for future cable additions.
Fill ratio is good!
Fill ratio is between 40% and 50%
Above the recommended fill ratio
An error exists

## Info (hidden)
Cable Type | O.D. | Hyperlink | Category | Notes | Pages without part numbers | Categories | Named Selection | Conduit Trade Size | I.D.
Select Category First |  |  |  |  | MCR | Select Category | SelectCategory | EMT 3/8 | 0.493 | Conduit1 | SelectCategory
SST Plenum | 0.25 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/LevBT_Spec_SST_Cat_6A_UTP_Plenum_Cable.pdf | Copper Structured Cables |  | MDP | Copper Structured Cables | CopperStructuredCables | EMT 1/2 | 0.622 | Conduit2 | SelectCategory
RDT Plenum | 0.23 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/LevBT_LM-RDT_Cat_6A_UTP_CMP_Cable.pdf | Copper Structured Cables |  | MDPK | Tight Buffer Fiber | TightBufferFiber | EMT 3/4 | 0.824 | Conduit3 | SelectCategory
RDT I/O Plenum | 0.235 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/LevBT_Spec_LM_RDT_IO_Cat6A_CMP_Cable.pdf | Copper Structured Cables |  |  | Loose Tube Fiber | LooseTubeFiber | EMT 1 | 1.049 | Conduit4 | SelectCategory
LANMARK™-2000 Plenum | 0.22 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/LevBT_LANmark-2000_Plenum.pdf | Copper Structured Cables |  |  | Ribbon Fiber | RibbonFiber | EMT 1-1/4 | 1.38 | Conduit5 | SelectCategory
LANMARK™-1000 Plenum | 0.225 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/LevBT_LANmark-1000_Plenum_Cable.pdf | Copper Structured Cables |  |  | Composite Fiber/Copper | CompositeFiberCopper | EMT 1-1/2 | 1.61 | Conduit6 | SelectCategory
LANMARK™-6 Plenum | 0.23 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/LevBT_LANmark-6_Plenum_Cable.pdf | Copper Structured Cables |  |  | Industrial Ethernet | IndustrialEthernet | EMT 2 | 2.067 | BasketTray1 | SelectCategory
LANMARK™-IP Plenum | 0.24 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/LevBT_LANmark-IP_5e.pdf | Copper Structured Cables |  |  |  |  | EMT 2-1/2 | 2.731 | BasketTray2 | SelectCategory
HyperPlus 5e Plenum | 0.21 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/LevBT_Hyper_Plus_Cat_5e_CMP_UTP_Cable.pdf | Copper Structured Cables |  |  |  |  | EMT 3 | 3.356 | BasketTray3 | SelectCategory
FDT Plenum | 0.235 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-FDT-Cat-6A-FUTP-CMP-Cable.pdf | Copper Structured Cables | [6 empty] | BasketTray4 | SelectCategory
LANMARK™-10G FTP Plenum | 0.275 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-LANMARK-10G-FTP-Plenum-Cable.pdf | Copper Structured Cables |  |  |  |  | EMT 3-1/2 | 3.834 | BasketTray5 | SelectCategory
LANMARK™-6 FTP Plenum | 0.275 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/LevBT_LANmark-6_FTP_Plenum.pdf | Copper Structured Cables |  |  |  |  | EMT 4 | 4.334 | BasketTray6 | SelectCategory
LANMARK™-HD Plenum | 0.275 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/LevBT_LANmark-HD_Plenum.pdf | Copper Structured Cables |  |  |  |  | IMC 1/2 | 0.675
|  |  | Copper Structured Cables | Dividers are a formula to ensure they show up as an empty space |  |  |  | IMC 3/4 | 0.879
SST Riser | 0.275 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/LevBT_Spec_SST_Cat_6A_UTP_Riser_Cable.pdf | Copper Structured Cables |  |  |  |  | IMC 1 | 1.12
RDT Riser | 0.245 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/LevBT_Spec_LM-RDT_Cat6A_UTP_CMR_Cable.pdf | Copper Structured Cables |  |  |  |  | IMC 1-1/4 | 1.468
LANMARK™-2000 Riser | 0.23 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/LevBT_LANmark-1000_Riser.pdf | Copper Structured Cables |  |  |  |  | IMC 1-1/2 | 1.703
LANMARK™-1000 Riser | 0.23 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/LevBT_LANmark-1000_Riser.pdf | Copper Structured Cables |  |  |  |  | IMC 2 | 2.17
LANMARK™-6 Riser | 0.205 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/LevBT_LANmark-6_Riser_Cable.pdf | Copper Structured Cables |  |  |  |  | IMC 2-1/2 | 2.597
HyperPlus 5e Riser | 0.19 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/LevBT_HyperPlus_5e_Riser_Rated_Category_5e_UTP.pdf | Copper Structured Cables |  |  |  |  | IMC 3 | 3.216
LANMARK™-10G FTP Riser | 0.29 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/LevBT_LANmark-10G_FTP_Riser.pdf | Copper Structured Cables |  |  |  |  | IMC 3-1/2 | 3.711
LANMARK™-6 FTP Riser | 0.28 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/LevBT_LANmark-6_FTP_Riser.pdf | Copper Structured Cables |  |  |  |  | IMC 4 | 4.206
LANMARK™-HD Riser | 0.28 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/LevBT_LANmark-HD_Riser.pdf | Copper Structured Cables |  |  |  |  | RMC 1/4 | 0.364
|  |  | Copper Structured Cables | Dividers are a formula to ensure they show up as an empty space |  |  |  | RMC 3/8 | 0.493
LANMARK™-10G OSP | 0.355 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/LevBT_LANmark-10G_Cat_6A_OSP.pdf | Copper Structured Cables
LANMARK™-1000 OSP | 0.245 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/LevBT_LANmark-1000_OSP.pdf | Copper Structured Cables
LANMARK™-6 OSP | 0.25 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/LevBT_LANmark-6_OSP.pdf | Copper Structured Cables
HyperPlus 5e OSP | 0.21 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/LevBT_HyperPlus_5e_OSP.pdf | Copper Structured Cables
|  |  |  | Dividers are a formula to ensure they show up as an empty space |  |  |  | RMC 1-1/2 | 1.624
ICP002-I/O | 0.17 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-Plenum-Premises-Distribution-Cable-ICP-IO.pdf | Tight Buffer Fiber |  |  |  |  | RMC 2 | 2.083
ICP004-I/O | 0.17 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-Plenum-Premises-Distribution-Cable-ICP-IO.pdf | Tight Buffer Fiber |  |  |  |  | RMC 2-1/2 | 2.489
PDP006-I/O | 0.17 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-Plenum-Premises-Distribution-Cable-PDP-IO.pdf | Tight Buffer Fiber |  |  |  |  | RMC 3 | 3.09
PDP012-I/O | 0.205 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-Plenum-Premises-Distribution-Cable-PDP-IO.pdf | Tight Buffer Fiber |  |  |  |  | RMC 3-1/2 | 3.57
PDP024-I/O | 0.275 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-Plenum-Premises-Distribution-Cable-PDP-IO.pdf | Tight Buffer Fiber |  |  |  |  | RMC 4 | 4.05
PDP12B036-I/O | 0.496 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-Plenum-Premises-Distribution-Cable-PDP-IO.pdf | Tight Buffer Fiber |  |  |  |  | RMC 4-1/2 | 4.506
PDP12B048-I/O | 0.558 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-Plenum-Premises-Distribution-Cable-PDP-IO.pdf | Tight Buffer Fiber |  |  |  |  | Sch40 1/8 | 0.249
PDP12B072-I/O | 0.671 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-Plenum-Premises-Distribution-Cable-PDP-IO.pdf | Tight Buffer Fiber |  |  |  |  | Sch40 1/4 | 0.334
PDP12B096-I/O | 0.859 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-Plenum-Premises-Distribution-Cable-PDP-IO.pdf | Tight Buffer Fiber |  |  |  |  | Sch40 3/8 | 0.473
PDP12B144-I/O | 0.896 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-Plenum-Premises-Distribution-Cable-PDP-IO.pdf | Tight Buffer Fiber |  |  |  |  | Sch40 1/2 | 0.602
|  |  | Tight Buffer Fiber | Dividers are a formula to ensure they show up as an empty space |  |  |  | Sch40 3/4 | 0.804
ICPK002-I/O | 0.495 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-Plenum-Premises-Distribution-Cable-Armortek-ICPK-IO.pdf | Tight Buffer Fiber |  |  |  |  | Sch40 1 | 1.029
ICPK004-I/O | 0.495 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-Plenum-Premises-Distribution-Cable-Armortek-ICPK-IO.pdf | Tight Buffer Fiber |  |  |  |  | Sch40 1-1/4 | 1.36
PDPK006-I/O | 0.495 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-Plenum-Premises-Distribution-Armortek-PDPK-IO.pdf | Tight Buffer Fiber |  |  |  |  | Sch40 1-1/2 | 1.59
PDPK012-I/O | 0.523 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-Plenum-Premises-Distribution-Armortek-PDPK-IO.pdf | Tight Buffer Fiber |  |  |  |  | Sch40 2 | 2.047
PDPK024-I/O | 0.584 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-Plenum-Premises-Distribution-Armortek-PDPK-IO.pdf | Tight Buffer Fiber |  |  |  |  | Sch40 2-1/2 | 2.445
PDPK12B036-I/O | 0.821 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-Plenum-Premises-Distribution-Armortek-PDPK-IO.pdf | Tight Buffer Fiber |  |  |  |  | Sch40 3 | 3.042
PDPK12B048-I/O | 0.921 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-Plenum-Premises-Distribution-Armortek-PDPK-IO.pdf | Tight Buffer Fiber |  |  |  |  | Sch40 3-1/2 | 3.521
PDPK12B072-I/O | 0.974 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-Plenum-Premises-Distribution-Armortek-PDPK-IO.pdf | Tight Buffer Fiber |  |  |  |  | Sch40 4 | 3.998
PDPK12B096-I/O | 1.225 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-Plenum-Premises-Distribution-Armortek-PDPK-IO.pdf | Tight Buffer Fiber |  |  |  |  | Sch40 5 | 5.016
PDPK12B144-I/O | 1.225 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-Plenum-Premises-Distribution-Armortek-PDPK-IO.pdf | Tight Buffer Fiber |  |  |  |  | Sch40 6 | 6.031
|  |  | Tight Buffer Fiber | Dividers are a formula to ensure they show up as an empty space |  |  |  | Sch80 1/8 | 0.195
PDP006-HE | 0.208 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-Plenum-Premises-Distribution-Cable-Harsh-Environments-PDP-HE.pdf | Tight Buffer Fiber |  |  |  |  | Sch80 1/4 | 0.282
PDP012-HE | 0.263 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-Plenum-Premises-Distribution-Cable-Harsh-Environments-PDP-HE.pdf | Tight Buffer Fiber |  |  |  |  | Sch80 3/8 | 0.403
PDP024-HE | 0.287 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-Plenum-Premises-Distribution-Cable-Harsh-Environments-PDP-HE.pdf | Tight Buffer Fiber |  |  |  |  | Sch80 1/2 | 0.526
PDP12B036-HE | 0.52 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-Plenum-Premises-Distribution-Cable-Harsh-Environments-PDP-HE.pdf | Tight Buffer Fiber |  |  |  |  | Sch80 3/4 | 0.722
PDP12B048-HE | 0.58 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-Plenum-Premises-Distribution-Cable-Harsh-Environments-PDP-HE.pdf | Tight Buffer Fiber |  |  |  |  | Sch80 1 | 0.936
PDP12B072-HE | 0.701 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-Plenum-Premises-Distribution-Cable-Harsh-Environments-PDP-HE.pdf | Tight Buffer Fiber |  |  |  |  | Sch80 1-1/4 | 1.255
PDP12B096-HE | 0.859 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-Plenum-Premises-Distribution-Cable-Harsh-Environments-PDP-HE.pdf | Tight Buffer Fiber |  |  |  |  | Sch80 1-1/2 | 1.476
PDP12B144-HE | 0.896 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-Plenum-Premises-Distribution-Cable-Harsh-Environments-PDP-HE.pdf | Tight Buffer Fiber |  |  |  |  | Sch80 2 | 1.913
|  |  | Tight Buffer Fiber | Dividers are a formula to ensure they show up as an empty space |  |  |  | Sch80 2-1/2 | 2.29
ICR002-I/O | 0.187 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-Riser-Premises-Distribution-Cable-ICR-IO.pdf | Tight Buffer Fiber |  |  |  |  | Sch80 3 | 2.864
ICR004-I/O | 0.187 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-Riser-Premises-Distribution-Cable-ICR-IO.pdf | Tight Buffer Fiber |  |  |  |  | Sch80 3-1/2 | 3.326
PDR006-I/O | 0.224 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-Riser-Premises-Distribution-Cable-PDR-IO.pdf | Tight Buffer Fiber |  |  |  |  | Sch80 4 | 3.786
PDR012-I/O | 0.246 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-Riser-Premises-Distribution-Cable-PDR-IO.pdf | Tight Buffer Fiber |  |  |  |  | Sch80 5 | 4.768
PDR024-I/O | 0.335 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-Riser-Premises-Distribution-Cable-PDR-IO.pdf | Tight Buffer Fiber |  |  |  |  | Sch80 6 | 5.709
PDR12B036-I/O | 0.555 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-Riser-Premises-Distribution-Cable-PDR-IO.pdf | Tight Buffer Fiber
PDR12B048-I/O | 0.59 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-Riser-Premises-Distribution-Cable-PDR-IO.pdf | Tight Buffer Fiber
PDR12B072-I/O | 0.732 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-Riser-Premises-Distribution-Cable-PDR-IO.pdf | Tight Buffer Fiber
PDR12B096-I/O | 0.88 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-Riser-Premises-Distribution-Cable-PDR-IO.pdf | Tight Buffer Fiber
PDR12B144-I/O | 0.94 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-Riser-Premises-Distribution-Cable-PDR-IO.pdf | Tight Buffer Fiber
|  |  | Tight Buffer Fiber | Dividers are a formula to ensure they show up as an empty space
PDRK006-I/O | 0.624 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-Riser-Premises-Distribution-Cable-Armortek-PDRK-IO.pdf | Tight Buffer Fiber
PDRK012-I/O | 0.624 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-Riser-Premises-Distribution-Cable-Armortek-PDRK-IO.pdf | Tight Buffer Fiber
PDRK024-I/O | 0.69 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-Riser-Premises-Distribution-Cable-Armortek-PDRK-IO.pdf | Tight Buffer Fiber
PDRK12B036-I/O | 0.961 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-Riser-Premises-Distribution-Cable-Armortek-PDRK-IO.pdf | Tight Buffer Fiber
PDRK12B048-I/O | 0.961 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-Riser-Premises-Distribution-Cable-Armortek-PDRK-IO.pdf | Tight Buffer Fiber
PDRK12B072-I/O | 1.08 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-Riser-Premises-Distribution-Cable-Armortek-PDRK-IO.pdf | Tight Buffer Fiber
PDRK12B144-I/O | 1.265 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-Riser-Premises-Distribution-Cable-Armortek-PDRK-IO.pdf | Tight Buffer Fiber
|  |  | Tight Buffer Fiber | Dividers are a formula to ensure they show up as an empty space
PDRZ006-I/O | 0.256 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-LSZH-Premises-Distribution-Cable-PDRZ-IO.pdf | Tight Buffer Fiber
PDRZ012-I/O | 0.278 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-LSZH-Premises-Distribution-Cable-PDRZ-IO.pdf | Tight Buffer Fiber
PDRZ024-I/O | 0.321 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-LSZH-Premises-Distribution-Cable-PDRZ-IO.pdf | Tight Buffer Fiber
PDRZ12B036-I/O | 0.555 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-LSZH-Premises-Distribution-Cable-PDRZ-IO.pdf | Tight Buffer Fiber
PDRZ12B048-I/O | 0.59 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-LSZH-Premises-Distribution-Cable-PDRZ-IO.pdf | Tight Buffer Fiber
|  |  | Tight Buffer Fiber | Dividers are a formula to ensure they show up as an empty space
ICP001 | 0.079 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Plenum-Interconnect-Cable-ICP.pdf | Tight Buffer Fiber
ICP002 | 0.17 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Plenum-Interconnect-Cable-ICP.pdf | Tight Buffer Fiber
ICP0X0 | 0.162 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Plenum-Interconnect-Cable-ICP.pdf | Tight Buffer Fiber | Used maximum component
ICP004 | 0.17 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Plenum-Interconnect-Cable-ICP.pdf | Tight Buffer Fiber
PDP006 | 0.168 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Plenum-Premises-Distribution-Cable-PDP.pdf | Tight Buffer Fiber
PDP012 | 0.2 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Plenum-Premises-Distribution-Cable-PDP.pdf | Tight Buffer Fiber
PDP024 | 0.265 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Plenum-Premises-Distribution-Cable-PDP.pdf | Tight Buffer Fiber
PDP12B036 | 0.496 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Plenum-Premises-Distribution-Cable-PDP.pdf | Tight Buffer Fiber
PDP12B048 | 0.558 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Plenum-Premises-Distribution-Cable-PDP.pdf | Tight Buffer Fiber
PDP12B072 | 0.671 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Plenum-Premises-Distribution-Cable-PDP.pdf | Tight Buffer Fiber
PDP12B096 | 0.859 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Plenum-Premises-Distribution-Cable-PDP.pdf | Tight Buffer Fiber
PDP12B144 | 0.896 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Plenum-Premises-Distribution-Cable-PDP.pdf | Tight Buffer Fiber
|  |  | Tight Buffer Fiber | Dividers are a formula to ensure they show up as an empty space
PDPK006 | 0.495 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Plenum-Premises-Distribution-Cable-Armortek-PDPK.pdf | Tight Buffer Fiber
PDPK012 | 0.523 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Plenum-Premises-Distribution-Cable-Armortek-PDPK.pdf | Tight Buffer Fiber
PDPK024 | 0.584 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Plenum-Premises-Distribution-Cable-Armortek-PDPK.pdf | Tight Buffer Fiber
PDPK12B036 | 0.821 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Plenum-Premises-Distribution-Cable-Armortek-PDPK.pdf | Tight Buffer Fiber
PDPK12B048 | 0.921 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Plenum-Premises-Distribution-Cable-Armortek-PDPK.pdf | Tight Buffer Fiber
PDPK12B072 | 0.974 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Plenum-Premises-Distribution-Cable-Armortek-PDPK.pdf | Tight Buffer Fiber
PDPK12B096 | 1.225 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Plenum-Premises-Distribution-Cable-Armortek-PDPK.pdf | Tight Buffer Fiber
PDPK12B144 | 1.225 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Plenum-Premises-Distribution-Cable-Armortek-PDPK.pdf | Tight Buffer Fiber
|  |  | Tight Buffer Fiber | Dividers are a formula to ensure they show up as an empty space
ICR001 | 0.079 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Riser-Interconnect-Cable-ICR.pdf | Tight Buffer Fiber
ICR002 | 0.187 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Riser-Interconnect-Cable-ICR.pdf | Tight Buffer Fiber
ICR0X0 | 0.162 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Riser-Interconnect-Cable-ICR.pdf | Tight Buffer Fiber | Used maximum component
ICR004 | 0.187 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Riser-Interconnect-Cable-ICR.pdf | Tight Buffer Fiber
PDR006 | 0.224 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Riser-Premises-Distribution-Cable-PDR.pdf | Tight Buffer Fiber
PDR012 | 0.246 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Riser-Premises-Distribution-Cable-PDR.pdf | Tight Buffer Fiber
PDR024 | 0.335 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Riser-Premises-Distribution-Cable-PDR.pdf | Tight Buffer Fiber
PDR12B036 | 0.555 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Riser-Premises-Distribution-Cable-PDR.pdf | Tight Buffer Fiber
PDR12B048 | 0.59 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Riser-Premises-Distribution-Cable-PDR.pdf | Tight Buffer Fiber
PDR12B072 | 0.732 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Riser-Premises-Distribution-Cable-PDR.pdf | Tight Buffer Fiber
PDR12B096 | 0.88 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Riser-Premises-Distribution-Cable-PDR.pdf | Tight Buffer Fiber
PDR12B144 | 0.94 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Riser-Premises-Distribution-Cable-PDR.pdf | Tight Buffer Fiber
|  |  | Tight Buffer Fiber | Dividers are a formula to ensure they show up as an empty space
PDRK006 | 0.624 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Riser-Premises-Distribution-Cable-Armortek-PDRK.pdf | Tight Buffer Fiber
PDRK012 | 0.624 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Riser-Premises-Distribution-Cable-Armortek-PDRK.pdf | Tight Buffer Fiber
PDRK024 | 0.69 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Riser-Premises-Distribution-Cable-Armortek-PDRK.pdf | Tight Buffer Fiber
PDRK12B036 | 0.961 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Riser-Premises-Distribution-Cable-Armortek-PDRK.pdf | Tight Buffer Fiber
PDRK12B048 | 0.961 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Riser-Premises-Distribution-Cable-Armortek-PDRK.pdf | Tight Buffer Fiber
PDRK12B072 | 1.08 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Riser-Premises-Distribution-Cable-Armortek-PDRK.pdf | Tight Buffer Fiber
PDRK12B096 | 1.265 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Riser-Premises-Distribution-Cable-Armortek-PDRK.pdf | Tight Buffer Fiber
PDRK12B144 | 1.265 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Riser-Premises-Distribution-Cable-Armortek-PDRK.pdf | Tight Buffer Fiber
|  |  | Tight Buffer Fiber | Dividers are a formula to ensure they show up as an empty space
PDRZ006 | 0.256 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-LSZH-Riser-Premises-Distribution-Cable-PDRZ.pdf | Tight Buffer Fiber
PDRZ012 | 0.278 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-LSZH-Riser-Premises-Distribution-Cable-PDRZ.pdf | Tight Buffer Fiber
PDRZ024 | 0.321 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-LSZH-Riser-Premises-Distribution-Cable-PDRZ.pdf | Tight Buffer Fiber
PDRZ12B036 | 0.555 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-LSZH-Riser-Premises-Distribution-Cable-PDRZ.pdf | Tight Buffer Fiber
PDRZ12B048 | 0.59 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-LSZH-Riser-Premises-Distribution-Cable-PDRZ.pdf | Tight Buffer Fiber
|  |  | Tight Buffer Fiber | Dividers are a formula to ensure they show up as an empty space
PDRZK006 | 0.656 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-LSZH-Riser-Premises-Distribution-Cable-Armortek-PDRZK.pdf | Tight Buffer Fiber
PDRZK012 | 0.656 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-LSZH-Riser-Premises-Distribution-Cable-Armortek-PDRZK.pdf | Tight Buffer Fiber
PDRZK024 | 0.696 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-LSZH-Riser-Premises-Distribution-Cable-Armortek-PDRZK.pdf | Tight Buffer Fiber
PDRZK12B036 | 1.005 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-LSZH-Riser-Premises-Distribution-Cable-Armortek-PDRZK.pdf | Tight Buffer Fiber
PDRZK12B048 | 1.005 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-LSZH-Riser-Premises-Distribution-Cable-Armortek-PDRZK.pdf | Tight Buffer Fiber
|  |  | Tight Buffer Fiber | Dividers are a formula to ensure they show up as an empty space
HDP002 | 0.235 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Plenum-Heavy-Duty-Breakout-Cable-HDP.pdf | Tight Buffer Fiber
HDP004 | 0.264 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Plenum-Heavy-Duty-Breakout-Cable-HDP.pdf | Tight Buffer Fiber
HDP006 | 0.317 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Plenum-Heavy-Duty-Breakout-Cable-HDP.pdf | Tight Buffer Fiber
HDP008 | 0.368 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Plenum-Heavy-Duty-Breakout-Cable-HDP.pdf | Tight Buffer Fiber
HDP012 | 0.472 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Plenum-Heavy-Duty-Breakout-Cable-HDP.pdf | Tight Buffer Fiber
HDP016 | 0.479 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Plenum-Heavy-Duty-Breakout-Cable-HDP.pdf | Tight Buffer Fiber
HDP018 | 0.479 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Plenum-Heavy-Duty-Breakout-Cable-HDP.pdf | Tight Buffer Fiber
HDP024 | 0.556 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Plenum-Heavy-Duty-Breakout-Cable-HDP.pdf | Tight Buffer Fiber
HDP032 | 0.641 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Plenum-Heavy-Duty-Breakout-Cable-HDP.pdf | Tight Buffer Fiber
HDP036 | 0.641 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Plenum-Heavy-Duty-Breakout-Cable-HDP.pdf | Tight Buffer Fiber
|  |  | Tight Buffer Fiber | Dividers are a formula to ensure they show up as an empty space
HDPK002 | 0.596 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-Plenum-CL3P-Cable-Armortek-HDPCK.pdf | Tight Buffer Fiber
HDPK004 | 0.596 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-Plenum-CL3P-Cable-Armortek-HDPCK.pdf | Tight Buffer Fiber
HDPK006 | 0.676 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-Plenum-CL3P-Cable-Armortek-HDPCK.pdf | Tight Buffer Fiber
HDPK008 | 0.726 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-Plenum-CL3P-Cable-Armortek-HDPCK.pdf | Tight Buffer Fiber
HDPK012 | 0.847 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-Plenum-CL3P-Cable-Armortek-HDPCK.pdf | Tight Buffer Fiber
HDPK016 | 0.847 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-Plenum-CL3P-Cable-Armortek-HDPCK.pdf | Tight Buffer Fiber
HDPK018 | 0.847 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-Plenum-CL3P-Cable-Armortek-HDPCK.pdf | Tight Buffer Fiber
HDPK024 | 0.947 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-Plenum-CL3P-Cable-Armortek-HDPCK.pdf | Tight Buffer Fiber
HDPK032 | 1 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-Plenum-CL3P-Cable-Armortek-HDPCK.pdf | Tight Buffer Fiber
HDPK036 | 1 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-Plenum-CL3P-Cable-Armortek-HDPCK.pdf | Tight Buffer Fiber
|  |  | Tight Buffer Fiber | Dividers are a formula to ensure they show up as an empty space
HDR002 | 0.268 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Riser-Heavy-Duty-Breakout-Cable-HDR.pdf | Tight Buffer Fiber
HDR004 | 0.268 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Riser-Heavy-Duty-Breakout-Cable-HDR.pdf | Tight Buffer Fiber
HDR006 | 0.315 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Riser-Heavy-Duty-Breakout-Cable-HDR.pdf | Tight Buffer Fiber
HDR008 | 0.376 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Riser-Heavy-Duty-Breakout-Cable-HDR.pdf | Tight Buffer Fiber
HDR012 | 0.47 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Riser-Heavy-Duty-Breakout-Cable-HDR.pdf | Tight Buffer Fiber
HDR016 | 0.487 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Riser-Heavy-Duty-Breakout-Cable-HDR.pdf | Tight Buffer Fiber
HDR018 | 0.487 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Riser-Heavy-Duty-Breakout-Cable-HDR.pdf | Tight Buffer Fiber
HDR024 | 0.614 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Riser-Heavy-Duty-Breakout-Cable-HDR.pdf | Tight Buffer Fiber
HDR032 | 0.649 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Riser-Heavy-Duty-Breakout-Cable-HDR.pdf | Tight Buffer Fiber
HDR036 | 0.699 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Riser-Heavy-Duty-Breakout-Cable-HDR.pdf | Tight Buffer Fiber
HDR048 | 0.864 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Riser-Heavy-Duty-Breakout-Cable-HDR.pdf | Tight Buffer Fiber
|  |  | Tight Buffer Fiber | Dividers are a formula to ensure they show up as an empty space
MCP001 | 0.063 |  | Tight Buffer Fiber
MCP002 | 0.094 |  | Tight Buffer Fiber
MCP0X0 | 0.13 |  | Tight Buffer Fiber | Used maximum component
Dividers are a formula to ensure they show up as an empty space
RDR12B024-I/O-M4 | 0.61 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-Riser-Ribbon-Cable-RDR-IO.pdf | Ribbon Fiber
RDR12B072-I/O-M4 | 0.67 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-Riser-Ribbon-Cable-RDR-IO.pdf | Ribbon Fiber
RDR12B096-I/O-M4 | 0.67 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-Riser-Ribbon-Cable-RDR-IO.pdf | Ribbon Fiber
RDR12B144-I/O-M4 | 0.67 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-Riser-Ribbon-Cable-RDR-IO.pdf | Ribbon Fiber
RDR36B576-I/O-M4 | 1.03 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-Riser-Ribbon-Cable-RDR-IO.pdf | Ribbon Fiber
RDR36B864-I/O-M4 | 1.03 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-Riser-Ribbon-Cable-RDR-IO.pdf | Ribbon Fiber
|  |  | Ribbon Fiber | Dividers are a formula to ensure they show up as an empty space
RDRZF12B048-I/O-M4 | 0.44 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-LSZH-Riser-Flex-Ribbon-Cable-RDRZF-IO.pdf | Ribbon Fiber
RDRZF12B072-I/O-M4 | 0.56 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-LSZH-Riser-Flex-Ribbon-Cable-RDRZF-IO.pdf | Ribbon Fiber
RDRZF12B096-I/O-M4 | 0.56 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-LSZH-Riser-Flex-Ribbon-Cable-RDRZF-IO.pdf | Ribbon Fiber
RDRZF12B144-I/O-M4 | 0.56 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-LSZH-Riser-Flex-Ribbon-Cable-RDRZF-IO.pdf | Ribbon Fiber
RDRZF12B192-I/O-M4 | 0.67 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-LSZH-Riser-Flex-Ribbon-Cable-RDRZF-IO.pdf | Ribbon Fiber
RDRZF12B288-I/O-M4 | 0.67 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-LSZH-Riser-Flex-Ribbon-Cable-RDRZF-IO.pdf | Ribbon Fiber
RDRZF12B432-I/O-M4 | 0.73 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-LSZH-Riser-Flex-Ribbon-Cable-RDRZF-IO.pdf | Ribbon Fiber
RDRZF12B576-I/O-M4 | 0.95 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-LSZH-Riser-Flex-Ribbon-Cable-RDRZF-IO.pdf | Ribbon Fiber
RDRZF12B864-I/O-M4 | 0.95 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-LSZH-Riser-Flex-Ribbon-Cable-RDRZF-IO.pdf | Ribbon Fiber
RDRZF12B1152-I/O-M4 | 1.06 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-LSZH-Riser-Flex-Ribbon-Cable-RDRZF-IO.pdf | Ribbon Fiber
RDRZF12B1728-I/O-M4 | 1.12 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-LSZH-Riser-Flex-Ribbon-Cable-RDRZF-IO.pdf | Ribbon Fiber
|  |  | Ribbon Fiber | Dividers are a formula to ensure they show up as an empty space
RDRK12B012-I/O(BLA)-M4 | 0.95 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-Riser-Ribbon-Cable-Armortek-RDRK-IO.pdf | Ribbon Fiber
RDRK12B024-I/O(BLA)-M4 | 0.95 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-Riser-Ribbon-Cable-Armortek-RDRK-IO.pdf | Ribbon Fiber
RDRK12B048-I/O(BLA)-M4 | 0.95 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-Riser-Ribbon-Cable-Armortek-RDRK-IO.pdf | Ribbon Fiber
RDRK12B096-I/O(BLA)-M4 | 0.99 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-Riser-Ribbon-Cable-Armortek-RDRK-IO.pdf | Ribbon Fiber
RDRK12B144-I/O(BLA)-M4 | 0.99 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-Riser-Ribbon-Cable-Armortek-RDRK-IO.pdf | Ribbon Fiber
|  |  | Ribbon Fiber | Dividers are a formula to ensure they show up as an empty space
RDP12B012-M4 | 0.44 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Plenum-Ribbon-Cable-RDP.pdf | Ribbon Fiber
RDP12B024-M4 | 0.44 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Plenum-Ribbon-Cable-RDP.pdf | Ribbon Fiber
RDP12B048-M4 | 0.44 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Plenum-Ribbon-Cable-RDP.pdf | Ribbon Fiber
RDP12B072-M4 | 0.55 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Plenum-Ribbon-Cable-RDP.pdf | Ribbon Fiber
RDP12B096-M4 | 0.55 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Plenum-Ribbon-Cable-RDP.pdf | Ribbon Fiber
RDP12B144-M4 | 0.65 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Plenum-Ribbon-Cable-RDP.pdf | Ribbon Fiber
RDP12B216-M4 | 0.65 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Plenum-Ribbon-Cable-RDP.pdf | Ribbon Fiber
RDP24B288-M4 | 0.85 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Plenum-Ribbon-Cable-RDP.pdf | Ribbon Fiber
RDP24B432-M4 | 0.85 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Plenum-Ribbon-Cable-RDP.pdf | Ribbon Fiber
|  |  | Ribbon Fiber | Dividers are a formula to ensure they show up as an empty space
RDPF12B072-M4 | 0.43 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Plenum-Flex-Ribbon-Cable-RDPF.pdf | Ribbon Fiber
RDPF12B144-M4 | 0.47 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Plenum-Flex-Ribbon-Cable-RDPF.pdf | Ribbon Fiber
RDPF12B216-M4 | 0.57 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Plenum-Flex-Ribbon-Cable-RDPF.pdf | Ribbon Fiber
RDPF12B288-M4 | 0.57 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Plenum-Flex-Ribbon-Cable-RDPF.pdf | Ribbon Fiber
|  |  | Ribbon Fiber | Dividers are a formula to ensure they show up as an empty space
RDPK12B048-M4 | 0.726 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Plenum-Ribbon-Cable-Armortek-RDPK.pdf | Ribbon Fiber
RDPK12B096-M4 | 0.851 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Plenum-Ribbon-Cable-Armortek-RDPK.pdf | Ribbon Fiber
RDPK12B144-M4 | 0.951 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Plenum-Ribbon-Cable-Armortek-RDPK.pdf | Ribbon Fiber
RDPK12B216-M4 | 0.951 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Plenum-Ribbon-Cable-Armortek-RDPK.pdf | Ribbon Fiber
RDPK12B288-M4 | 1.241 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Plenum-Ribbon-Cable-Armortek-RDPK.pdf | Ribbon Fiber
RDPK12B432-M4 | 1.241 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Plenum-Ribbon-Cable-Armortek-RDPK.pdf | Ribbon Fiber
|  |  | Ribbon Fiber | Dividers are a formula to ensure they show up as an empty space
RDR12B012-M4 | 0.52 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Riser-Ribbon-Cable-RDR.pdf | Ribbon Fiber
RDR12B048-M4 | 0.52 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Riser-Ribbon-Cable-RDR.pdf | Ribbon Fiber
RDR12B072-M4 | 0.52 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Riser-Ribbon-Cable-RDR.pdf | Ribbon Fiber
RDR12B096-M4 | 0.52 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Riser-Ribbon-Cable-RDR.pdf | Ribbon Fiber
RDR12B144-M4 | 0.62 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Riser-Ribbon-Cable-RDR.pdf | Ribbon Fiber
RDR12B216-M4 | 0.62 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Riser-Ribbon-Cable-RDR.pdf | Ribbon Fiber
RDR24B288-M4 | 0.81 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Riser-Ribbon-Cable-RDR.pdf | Ribbon Fiber
RDR24B432-M4 | 0.81 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Riser-Ribbon-Cable-RDR.pdf | Ribbon Fiber
|  |  | Ribbon Fiber | Dividers are a formula to ensure they show up as an empty space
RDRF12B144-M4 | 0.4 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Riser-Flex-Ribbon-Cable-RDRF.pdf | Ribbon Fiber
RDRF12B288-M4 | 0.57 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Riser-Flex-Ribbon-Cable-RDRF.pdf | Ribbon Fiber
|  |  | Ribbon Fiber | Dividers are a formula to ensure they show up as an empty space
RDRK12B048-M4 | 0.854 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Riser-Ribbon-Cable-Armortek-RDRK.pdf | Ribbon Fiber
RDRK12B096-M4 | 0.854 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Riser-Ribbon-Cable-Armortek-RDRK.pdf | Ribbon Fiber
RDRK12B144-M4 | 0.947 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Riser-Ribbon-Cable-Armortek-RDRK.pdf | Ribbon Fiber
RDRK12B216-M4 | 0.947 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Riser-Ribbon-Cable-Armortek-RDRK.pdf | Ribbon Fiber
RDRK12B288-M4 | 0.947 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Riser-Ribbon-Cable-Armortek-RDRK.pdf | Ribbon Fiber
RDRK12B432-M4 | 1.138 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Riser-Ribbon-Cable-Armortek-RDRK.pdf | Ribbon Fiber
RDRK12B576-M4 | 1.33 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Riser-Ribbon-Cable-Armortek-RDRK.pdf | Ribbon Fiber
RDRK12B864-M4 | 1.33 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Riser-Ribbon-Cable-Armortek-RDRK.pdf | Ribbon Fiber
|  |  | Ribbon Fiber | Dividers are a formula to ensure they show up as an empty space
RDOA12B048-M4 | 0.48 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Outdoor-Armored-Ribbon-Cable-RDOA.pdf | Ribbon Fiber
RDOA12B096-M4 | 0.58 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Outdoor-Armored-Ribbon-Cable-RDOA.pdf | Ribbon Fiber
RDOA12B144-M4 | 0.64 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Outdoor-Armored-Ribbon-Cable-RDOA.pdf | Ribbon Fiber
RDOA12B216-M4 | 0.8 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Outdoor-Armored-Ribbon-Cable-RDOA.pdf | Ribbon Fiber
RDOA12B288-M4 | 0.86 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Outdoor-Armored-Ribbon-Cable-RDOA.pdf | Ribbon Fiber
RDOA12B432-M4 | 0.97 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Outdoor-Armored-Ribbon-Cable-RDOA.pdf | Ribbon Fiber
Dividers are a formula to ensure they show up as an empty space
LTP006 | 0.26 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-IO-Plenum-Adventum-LTP.pdf | Loose Tube Fiber
LTP012 | 0.26 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-IO-Plenum-Adventum-LTP.pdf | Loose Tube Fiber
LTP12B024 | 0.37 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-IO-Plenum-Adventum-LTP.pdf | Loose Tube Fiber
LTP12B048 | 0.37 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-IO-Plenum-Adventum-LTP.pdf | Loose Tube Fiber
LTP12B072 | 0.46 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-IO-Plenum-Adventum-LTP.pdf | Loose Tube Fiber
LTP12B096 | 0.532 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-IO-Plenum-Adventum-LTP.pdf | Loose Tube Fiber
LTP12B144 | 0.67 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-IO-Plenum-Adventum-LTP.pdf | Loose Tube Fiber
LTP12B288 | 0.825 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-IO-Plenum-Adventum-LTP.pdf | Loose Tube Fiber
LTP12B432 | 0.94 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-IO-Plenum-Adventum-LTP.pdf | Loose Tube Fiber
|  |  | Loose Tube Fiber | Dividers are a formula to ensure they show up as an empty space
LTPK006 | 0.62 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-IO-Plenum-Adventum-ArmorTek-LTPK.pdf | Loose Tube Fiber
LTPK012 | 0.62 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-IO-Plenum-Adventum-ArmorTek-LTPK.pdf | Loose Tube Fiber
LTPK12B012 | 0.73 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-IO-Plenum-Adventum-ArmorTek-LTPK.pdf | Loose Tube Fiber
LTPK12B024 | 0.73 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-IO-Plenum-Adventum-ArmorTek-LTPK.pdf | Loose Tube Fiber
LTPK12B036 | 0.73 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-IO-Plenum-Adventum-ArmorTek-LTPK.pdf | Loose Tube Fiber
LTPK12B048 | 0.73 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-IO-Plenum-Adventum-ArmorTek-LTPK.pdf | Loose Tube Fiber
LTPK12B072 | 0.774 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-IO-Plenum-Adventum-ArmorTek-LTPK.pdf | Loose Tube Fiber
LTPK12B096 | 0.851 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-IO-Plenum-Adventum-ArmorTek-LTPK.pdf | Loose Tube Fiber
LTPK12B144 | 1.004 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-IO-Plenum-Adventum-ArmorTek-LTPK.pdf | Loose Tube Fiber
LTPK12B288 | 1.148 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-IO-Plenum-Adventum-ArmorTek-LTPK.pdf | Loose Tube Fiber
LTPK12B432 | 1.295 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-IO-Plenum-Adventum-ArmorTek-LTPK.pdf | Loose Tube Fiber
|  |  | Loose Tube Fiber | Dividers are a formula to ensure they show up as an empty space
LTP12B006-HE | 0.46 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-IO-Plenum-Adventum-Harsh-Environment-LTP-HE.pdf | Loose Tube Fiber
LTP12B012-HE | 0.46 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-IO-Plenum-Adventum-Harsh-Environment-LTP-HE.pdf | Loose Tube Fiber
LTP12B024-HE | 0.46 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-IO-Plenum-Adventum-Harsh-Environment-LTP-HE.pdf | Loose Tube Fiber
LTP12B048-HE | 0.46 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-IO-Plenum-Adventum-Harsh-Environment-LTP-HE.pdf | Loose Tube Fiber
LTP12B072-HE | 0.46 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-IO-Plenum-Adventum-Harsh-Environment-LTP-HE.pdf | Loose Tube Fiber
LTP12B096-HE | 0.532 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-IO-Plenum-Adventum-Harsh-Environment-LTP-HE.pdf | Loose Tube Fiber
LTP12B144-HE | 0.67 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-IO-Plenum-Adventum-Harsh-Environment-LTP-HE.pdf | Loose Tube Fiber
|  |  | Loose Tube Fiber | Dividers are a formula to ensure they show up as an empty space
LTR006 | 0.255 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-IO-Riser-Adventum-LTR.pdf | Loose Tube Fiber
LTR012 | 0.255 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-IO-Riser-Adventum-LTR.pdf | Loose Tube Fiber
LTR12B012 | 0.396 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-IO-Riser-Adventum-LTR.pdf | Loose Tube Fiber
LTR12B024 | 0.396 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-IO-Riser-Adventum-LTR.pdf | Loose Tube Fiber
LTR12B048 | 0.396 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-IO-Riser-Adventum-LTR.pdf | Loose Tube Fiber
LTR12B072 | 0.467 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-IO-Riser-Adventum-LTR.pdf | Loose Tube Fiber
LTR12B096 | 0.541 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-IO-Riser-Adventum-LTR.pdf | Loose Tube Fiber
LTR12B144 | 0.696 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-IO-Riser-Adventum-LTR.pdf | Loose Tube Fiber
LTR12B288 | 0.826 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-IO-Riser-Adventum-LTR.pdf | Loose Tube Fiber
LTR12B432 | 0.953 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-IO-Riser-Adventum-LTR.pdf | Loose Tube Fiber
|  |  | Loose Tube Fiber | Dividers are a formula to ensure they show up as an empty space
LTRK006 | 0.636 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-IO-Riser-Adventum-ArmorTek-LTRK.pdf | Loose Tube Fiber
LTRK012 | 0.636 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-IO-Riser-Adventum-ArmorTek-LTRK.pdf | Loose Tube Fiber
LTRK12B012 | 0.744 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-IO-Riser-Adventum-ArmorTek-LTRK.pdf | Loose Tube Fiber
LTRK12B024 | 0.744 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-IO-Riser-Adventum-ArmorTek-LTRK.pdf | Loose Tube Fiber
LTRK12B048 | 0.744 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-IO-Riser-Adventum-ArmorTek-LTRK.pdf | Loose Tube Fiber
LTRK12B072 | 0.865 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-IO-Riser-Adventum-ArmorTek-LTRK.pdf | Loose Tube Fiber
LTRK12B096 | 0.965 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-IO-Riser-Adventum-ArmorTek-LTRK.pdf | Loose Tube Fiber
LTRK12B144 | 1.018 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-IO-Riser-Adventum-ArmorTek-LTRK.pdf | Loose Tube Fiber
LTRK12B288 | 1.134 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-IO-Riser-Adventum-ArmorTek-LTRK.pdf | Loose Tube Fiber
LTRK12B432 | 1.269 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-IO-Riser-Adventum-ArmorTek-LTRK.pdf | Loose Tube Fiber
|  |  | Loose Tube Fiber | Dividers are a formula to ensure they show up as an empty space
LTRA12B006 | 0.575 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-IO-Riser-Adventum-SADJ-LTRA.pdf | Loose Tube Fiber
LTRA12B012 | 0.575 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-IO-Riser-Adventum-SADJ-LTRA.pdf | Loose Tube Fiber
LTRA12B024 | 0.575 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-IO-Riser-Adventum-SADJ-LTRA.pdf | Loose Tube Fiber
LTRA12B048 | 0.575 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-IO-Riser-Adventum-SADJ-LTRA.pdf | Loose Tube Fiber
LTRA12B072 | 0.646 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-IO-Riser-Adventum-SADJ-LTRA.pdf | Loose Tube Fiber
LTRA12B096 | 0.714 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-IO-Riser-Adventum-SADJ-LTRA.pdf | Loose Tube Fiber
LTRA12B144 | 0.869 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-IO-Riser-Adventum-SADJ-LTRA.pdf | Loose Tube Fiber
LTRA12B288 | 0.999 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-IO-Riser-Adventum-SADJ-LTRA.pdf | Loose Tube Fiber
|  |  | Loose Tube Fiber | Dividers are a formula to ensure they show up as an empty space
LTRZ006 | 0.237 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-LSZH-Riser-Adventum-Cable-LTRZ.pdf | Loose Tube Fiber
LTRZ012 | 0.237 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-LSZH-Riser-Adventum-Cable-LTRZ.pdf | Loose Tube Fiber
LTRZ12B012 | 0.39 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-LSZH-Riser-Adventum-Cable-LTRZ.pdf | Loose Tube Fiber
LTRZ12B024 | 0.39 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-LSZH-Riser-Adventum-Cable-LTRZ.pdf | Loose Tube Fiber
LTRZ12B048 | 0.39 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-LSZH-Riser-Adventum-Cable-LTRZ.pdf | Loose Tube Fiber
LTRZ12B072 | 0.467 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-LSZH-Riser-Adventum-Cable-LTRZ.pdf | Loose Tube Fiber
LTRZ12B096 | 0.541 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-LSZH-Riser-Adventum-Cable-LTRZ.pdf | Loose Tube Fiber
LTRZ12B144 | 0.696 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-LSZH-Riser-Adventum-Cable-LTRZ.pdf | Loose Tube Fiber
LTRZ12B288 | 0.818 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-LSZH-Riser-Adventum-Cable-LTRZ.pdf | Loose Tube Fiber
LTRZ12B432 | 0.953 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-LSZH-Riser-Adventum-Cable-LTRZ.pdf | Loose Tube Fiber
|  |  | Loose Tube Fiber | Dividers are a formula to ensure they show up as an empty space
LTRZK006 | 0.618 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-LSZH-Riser-Adventum-Cable-Armortek-LTRZK.pdf | Loose Tube Fiber
LTRZK012 | 0.618 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-LSZH-Riser-Adventum-Cable-Armortek-LTRZK.pdf | Loose Tube Fiber
LTRZK12B012 | 0.744 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-LSZH-Riser-Adventum-Cable-Armortek-LTRZK.pdf | Loose Tube Fiber
LTRZK12B024 | 0.744 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-LSZH-Riser-Adventum-Cable-Armortek-LTRZK.pdf | Loose Tube Fiber
LTRZK12B048 | 0.744 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-LSZH-Riser-Adventum-Cable-Armortek-LTRZK.pdf | Loose Tube Fiber
LTRZK12B072 | 0.865 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-LSZH-Riser-Adventum-Cable-Armortek-LTRZK.pdf | Loose Tube Fiber
LTRZK12B096 | 0.965 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-LSZH-Riser-Adventum-Cable-Armortek-LTRZK.pdf | Loose Tube Fiber
LTRZK12B144 | 1.084 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-LSZH-Riser-Adventum-Cable-Armortek-LTRZK.pdf | Loose Tube Fiber
LTRZK12B288 | 1.134 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-LSZH-Riser-Adventum-Cable-Armortek-LTRZK.pdf | Loose Tube Fiber
LTRZK12B432 | 1.269 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-LSZH-Riser-Adventum-Cable-Armortek-LTRZK.pdf | Loose Tube Fiber
|  |  | Loose Tube Fiber | Dividers are a formula to ensure they show up as an empty space
LTRZA12B006 | 0.563 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-LSZH-Riser-Adventum-SADJ-Cable-LTRZA.pdf | Loose Tube Fiber
LTRZA12B012 | 0.563 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-LSZH-Riser-Adventum-SADJ-Cable-LTRZA.pdf | Loose Tube Fiber
LTRZA12B024 | 0.563 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-LSZH-Riser-Adventum-SADJ-Cable-LTRZA.pdf | Loose Tube Fiber
LTRZA12B048 | 0.563 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-LSZH-Riser-Adventum-SADJ-Cable-LTRZA.pdf | Loose Tube Fiber
LTRZA12B072 | 0.64 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-LSZH-Riser-Adventum-SADJ-Cable-LTRZA.pdf | Loose Tube Fiber
LTRZA12B096 | 0.714 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-LSZH-Riser-Adventum-SADJ-Cable-LTRZA.pdf | Loose Tube Fiber
LTRZA12B144 | 0.869 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-LSZH-Riser-Adventum-SADJ-Cable-LTRZA.pdf | Loose Tube Fiber
LTRZA12B288 | 0.999 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-LSZH-Riser-Adventum-SADJ-Cable-LTRZA.pdf | Loose Tube Fiber
|  |  | Loose Tube Fiber | Dividers are a formula to ensure they show up as an empty space
SJP012-2J | 0.188 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-OPT-X-SJP-Plenum-Loose-Tube-Cable.pdf | Loose Tube Fiber
SJP12B024 | 0.296 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-OPT-X-SJP-Plenum-Loose-Tube-Cable.pdf | Loose Tube Fiber
SJP12B048 | 0.296 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-OPT-X-SJP-Plenum-Loose-Tube-Cable.pdf | Loose Tube Fiber
SJP12B072 | 0.32 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-OPT-X-SJP-Plenum-Loose-Tube-Cable.pdf | Loose Tube Fiber
SJP8B096 | 0.42 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-OPT-X-SJP-Plenum-Loose-Tube-Cable.pdf | Loose Tube Fiber
SJP12B096 | 0.42 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-OPT-X-SJP-Plenum-Loose-Tube-Cable.pdf | Loose Tube Fiber
SJP12B144 | 0.42 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-OPT-X-SJP-Plenum-Loose-Tube-Cable.pdf | Loose Tube Fiber
SJP12B288 | 0.64 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-OPT-X-SJP-Plenum-Loose-Tube-Cable.pdf | Loose Tube Fiber
|  |  | Loose Tube Fiber | Dividers are a formula to ensure they show up as an empty space
SJPK012-2J | 0.563 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-OPT-X-SJPK-Plenum-Loose-Tube-Cable-with-ARMOR-TEK.pdf | Loose Tube Fiber
SJPK12B024 | 0.614 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-OPT-X-SJPK-Plenum-Loose-Tube-Cable-with-ARMOR-TEK.pdf | Loose Tube Fiber
SJPK12B048 | 0.614 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-OPT-X-SJPK-Plenum-Loose-Tube-Cable-with-ARMOR-TEK.pdf | Loose Tube Fiber
SJPK12B072 | 0.68 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-OPT-X-SJPK-Plenum-Loose-Tube-Cable-with-ARMOR-TEK.pdf | Loose Tube Fiber
SJPK8B096 | 0.774 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-OPT-X-SJPK-Plenum-Loose-Tube-Cable-with-ARMOR-TEK.pdf | Loose Tube Fiber
SJPK12B096 | 0.774 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-OPT-X-SJPK-Plenum-Loose-Tube-Cable-with-ARMOR-TEK.pdf | Loose Tube Fiber
SJPK12B144 | 0.774 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-OPT-X-SJPK-Plenum-Loose-Tube-Cable-with-ARMOR-TEK.pdf | Loose Tube Fiber
SJPK12B288 | 0.951 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-OPT-X-SJPK-Plenum-Loose-Tube-Cable-with-ARMOR-TEK.pdf | Loose Tube Fiber
|  |  | Loose Tube Fiber | Dividers are a formula to ensure they show up as an empty space
DAP12B012 | 0.074 |  | Loose Tube Fiber
DAP12B012-2J | 0.177 |  | Loose Tube Fiber
DAP12B024 | 0.232 |  | Loose Tube Fiber | Used maximum component
DAP12B024-TWINAX | 0.184 |  | Loose Tube Fiber
DAP12B048 | 0.232 |  | Loose Tube Fiber
DAP12B072 | 0.261 |  | Loose Tube Fiber
DAP12B096 | 0.318 |  | Loose Tube Fiber
DAP12B144 | 0.376 |  | Loose Tube Fiber
DAP12B288 | 0.576 |  | Loose Tube Fiber
|  |  | Loose Tube Fiber | Dividers are a formula to ensure they show up as an empty space
DAP8B008 | 0.074 |  | Loose Tube Fiber
DAP8B008-2J | 0.177 |  | Loose Tube Fiber
DAP8B016 | 0.212 |  | Loose Tube Fiber
DAP8B024 | 0.212 |  | Loose Tube Fiber
DAP8B032 | 0.212 |  | Loose Tube Fiber
DAP8B048 | 0.261 |  | Loose Tube Fiber
DAP8B072 | 0.352 |  | Loose Tube Fiber
DAP8B096 | 0.376 |  | Loose Tube Fiber
DAP8B144 | 0.435 |  | Loose Tube Fiber
DAP8B288 | 0.625 |  | Loose Tube Fiber
|  |  | Loose Tube Fiber | Dividers are a formula to ensure they show up as an empty space
DAPK12B012-2J | 0.535 |  | Loose Tube Fiber | Used maximum component
DAPK12B024 | 0.553 |  | Loose Tube Fiber
DAPK12B024-TWINAX | 0.553 |  | Loose Tube Fiber | Used maximum component
DAPK12B048 | 0.553 |  | Loose Tube Fiber
DAPK12B072 | 0.614 |  | Loose Tube Fiber
DAPK12B096 | 0.68 |  | Loose Tube Fiber
DAPK12B144 | 0.73 |  | Loose Tube Fiber
DAPK12B288 | 0.951 |  | Loose Tube Fiber
|  |  | Loose Tube Fiber | Dividers are a formula to ensure they show up as an empty space
DAPK8B008-2J | 0.535 |  | Loose Tube Fiber
DAPK8B016 | 0.553 |  | Loose Tube Fiber
DAPK8B024 | 0.553 |  | Loose Tube Fiber
DAPK8B032 | 0.553 |  | Loose Tube Fiber
DAPK8B048 | 0.614 |  | Loose Tube Fiber
DAPK8B072 | 0.68 |  | Loose Tube Fiber
DAPK8B096 | 0.73 |  | Loose Tube Fiber
DAPK8B144 | 0.774 |  | Loose Tube Fiber
DAPK8B288 | 0.951 |  | Loose Tube Fiber
|  |  | Loose Tube Fiber | Dividers are a formula to ensure they show up as an empty space
ACP006 | 0.118 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Plenum-High-Density-Distribution-Cable-ACP.pdf | Loose Tube Fiber
ACP012 | 0.118 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Plenum-High-Density-Distribution-Cable-ACP.pdf | Loose Tube Fiber
ACP012-2J | 0.26 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Plenum-High-Density-Distribution-Cable-ACP.pdf | Loose Tube Fiber
|  |  | Loose Tube Fiber | Dividers are a formula to ensure they show up as an empty space
LTD12B006-M2 | 0.39 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Outside-Plant-Dry-Loose-Tube-Cable-LTD-M2.pdf | Loose Tube Fiber
LTD12B012-M2 | 0.39 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Outside-Plant-Dry-Loose-Tube-Cable-LTD-M2.pdf | Loose Tube Fiber
LTD12B024-M2 | 0.39 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Outside-Plant-Dry-Loose-Tube-Cable-LTD-M2.pdf | Loose Tube Fiber
LTD12B036-M2 | 0.39 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Outside-Plant-Dry-Loose-Tube-Cable-LTD-M2.pdf | Loose Tube Fiber
LTD12B048-M2 | 0.39 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Outside-Plant-Dry-Loose-Tube-Cable-LTD-M2.pdf | Loose Tube Fiber
LTD12B060-M2 | 0.39 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Outside-Plant-Dry-Loose-Tube-Cable-LTD-M2.pdf | Loose Tube Fiber
LTD12B072-M2 | 0.41 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Outside-Plant-Dry-Loose-Tube-Cable-LTD-M2.pdf | Loose Tube Fiber
LTD12B096-M2 | 0.48 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Outside-Plant-Dry-Loose-Tube-Cable-LTD-M2.pdf | Loose Tube Fiber
LTD12B120-M2 | 0.55 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Outside-Plant-Dry-Loose-Tube-Cable-LTD-M2.pdf | Loose Tube Fiber
LTD12B144-M2 | 0.62 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Outside-Plant-Dry-Loose-Tube-Cable-LTD-M2.pdf | Loose Tube Fiber
LTD12B216-M2 | 0.61 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Outside-Plant-Dry-Loose-Tube-Cable-LTD-M2.pdf | Loose Tube Fiber
LTD12B288-M2 | 0.71 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Outside-Plant-Dry-Loose-Tube-Cable-LTD-M2.pdf | Loose Tube Fiber
|  |  | Loose Tube Fiber | Dividers are a formula to ensure they show up as an empty space
LTAD12B006-1A1J-M2 | 0.46 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Outside-Plant-Dry-Loose-Tube-SADJ-Cable-LTAD-1A1J-M2.pdf | Loose Tube Fiber
LTAD12B012-1A1J-M2 | 0.46 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Outside-Plant-Dry-Loose-Tube-SADJ-Cable-LTAD-1A1J-M2.pdf | Loose Tube Fiber
LTAD12B024-1A1J-M2 | 0.46 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Outside-Plant-Dry-Loose-Tube-SADJ-Cable-LTAD-1A1J-M2.pdf | Loose Tube Fiber
LTAD12B036-1A1J-M2 | 0.46 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Outside-Plant-Dry-Loose-Tube-SADJ-Cable-LTAD-1A1J-M2.pdf | Loose Tube Fiber
LTAD12B048-1A1J-M2 | 0.46 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Outside-Plant-Dry-Loose-Tube-SADJ-Cable-LTAD-1A1J-M2.pdf | Loose Tube Fiber
LTAD12B060-1A1J-M2 | 0.46 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Outside-Plant-Dry-Loose-Tube-SADJ-Cable-LTAD-1A1J-M2.pdf | Loose Tube Fiber
LTAD12B072-1A1J-M2 | 0.48 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Outside-Plant-Dry-Loose-Tube-SADJ-Cable-LTAD-1A1J-M2.pdf | Loose Tube Fiber
LTAD12B096-1A1J-M2 | 0.55 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Outside-Plant-Dry-Loose-Tube-SADJ-Cable-LTAD-1A1J-M2.pdf | Loose Tube Fiber
LTAD12B120-1A1J-M2 | 0.62 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Outside-Plant-Dry-Loose-Tube-SADJ-Cable-LTAD-1A1J-M2.pdf | Loose Tube Fiber
LTAD12B144-1A1J-M2 | 0.69 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Outside-Plant-Dry-Loose-Tube-SADJ-Cable-LTAD-1A1J-M2.pdf | Loose Tube Fiber
LTAD12B216-1A1J-M2 | 0.68 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Outside-Plant-Dry-Loose-Tube-SADJ-Cable-LTAD-1A1J-M2.pdf | Loose Tube Fiber
LTAD12B288-1A1J-M2 | 0.78 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Outside-Plant-Dry-Loose-Tube-SADJ-Cable-LTAD-1A1J-M2.pdf | Loose Tube Fiber
|  |  | Loose Tube Fiber | Dividers are a formula to ensure they show up as an empty space
OPD006 | 0.4 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Outside-Plant-All-Dielectric-Cable-OPD.pdf | Loose Tube Fiber
OPD012 | 0.4 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Outside-Plant-All-Dielectric-Cable-OPD.pdf | Loose Tube Fiber
OPDD12B024 | 0.451 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Outside-Plant-All-Dielectric-Cable-OPDD.pdf | Loose Tube Fiber
OPDD12B048 | 0.451 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Outside-Plant-All-Dielectric-Cable-OPDD.pdf | Loose Tube Fiber
OPDD12B072 | 0.489 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Outside-Plant-All-Dielectric-Cable-OPDD.pdf | Loose Tube Fiber
OPDD12B096 | 0.565 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Outside-Plant-All-Dielectric-Cable-OPDD.pdf | Loose Tube Fiber
OPDD12B144 | 0.716 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Outside-Plant-All-Dielectric-Cable-OPDD.pdf | Loose Tube Fiber
OPDD12B216 | 0.74 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Outside-Plant-All-Dielectric-Cable-OPDD.pdf | Loose Tube Fiber
OPDD12B288 | 0.837 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Outside-Plant-All-Dielectric-Cable-OPDD.pdf | Loose Tube Fiber
|  |  | Loose Tube Fiber | Dividers are a formula to ensure they show up as an empty space
OPA006 | 0.57 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Outside-Plant-SADJ-Cable-OPA.pdf | Loose Tube Fiber
OPA012 | 0.57 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Outside-Plant-SADJ-Cable-OPA.pdf | Loose Tube Fiber
OPAD12B024 | 0.621 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Outside-Plant-SADJ-Cable-OPAD.pdf | Loose Tube Fiber
OPAD12B048 | 0.621 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Outside-Plant-SADJ-Cable-OPAD.pdf | Loose Tube Fiber
OPAD12B072 | 0.659 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Outside-Plant-SADJ-Cable-OPAD.pdf | Loose Tube Fiber
OPAD12B096 | 0.745 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Outside-Plant-SADJ-Cable-OPAD.pdf | Loose Tube Fiber
OPAD12B144 | 0.896 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Outside-Plant-SADJ-Cable-OPAD.pdf | Loose Tube Fiber
OPAD12B216 | 0.92 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Outside-Plant-SADJ-Cable-OPAD.pdf | Loose Tube Fiber
Dividers are a formula to ensure they show up as an empty space
HDPC002-002X12AWG | 0.314 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-Plenum-CL3P-Cable-HDPC.pdf | Composite Fiber/Copper
ACPC002-002X12AWG | 0.328 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-Plenum-CL3P-Cable-ACPC.pdf | Composite Fiber/Copper
ACPC004-002X12AWG | 0.328 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-Plenum-CL3P-Cable-ACPC.pdf | Composite Fiber/Copper
ACPC004-004X12AWG | 0.393 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-Plenum-CL3P-Cable-ACPC.pdf | Composite Fiber/Copper
ACPC006-002X12AWG | 0.328 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-Plenum-CL3P-Cable-ACPC.pdf | Composite Fiber/Copper
ACPC008-002X12AWG | 0.328 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-Plenum-CL3P-Cable-ACPC.pdf | Composite Fiber/Copper
ACPC008-004X12AWG | 0.393 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-Plenum-CL3P-Cable-ACPC.pdf | Composite Fiber/Copper
ACPC012-002X12AWG | 0.328 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-Plenum-CL3P-Cable-ACPC.pdf | Composite Fiber/Copper
ACPC012-004X12AWG | 0.393 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-Plenum-CL3P-Cable-ACPC.pdf | Composite Fiber/Copper
|  |  | Composite Fiber/Copper | Dividers are a formula to ensure they show up as an empty space
HDPCK002-002X12AWG | 0.67 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-Plenum-CL3P-Cable-Armortek-HDPCK.pdf | Composite Fiber/Copper
ACPCK004-002X12AWG | 0.67 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-Plenum-CL3P-Cable-Armortek-ACPCK.pdf | Composite Fiber/Copper
ACPCK004-004X12AWG | 0.72 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-Plenum-CL3P-Cable-Armortek-ACPCK.pdf | Composite Fiber/Copper
ACPCK006-002X12AWG | 0.67 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-Plenum-CL3P-Cable-Armortek-ACPCK.pdf | Composite Fiber/Copper
ACPCK006-003X12AWG | 0.72 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-Plenum-CL3P-Cable-Armortek-ACPCK.pdf | Composite Fiber/Copper
ACPCK008-004X12AWG | 0.72 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-Plenum-CL3P-Cable-Armortek-ACPCK.pdf | Composite Fiber/Copper
ACPCK012-002X12AWG | 0.67 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-Plenum-CL3P-Cable-Armortek-ACPCK.pdf | Composite Fiber/Copper
ACPCK012-004X12AWG | 0.72 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-Plenum-CL3P-Cable-Armortek-ACPCK.pdf | Composite Fiber/Copper
|  |  | Composite Fiber/Copper | Dividers are a formula to ensure they show up as an empty space
HDRC002-002X12AWG | 0.34 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-Riser-CL3R-HDRC-Cable.pdf | Composite Fiber/Copper
HDRC002-004X12AWG | 0.462 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-Riser-CL3R-HDRC-Cable.pdf | Composite Fiber/Copper
ACRC002-002X12AWG | 0.375 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-Riser-CL3P-Cable-ACRC.pdf | Composite Fiber/Copper
ACRC004-002X12AWG | 0.375 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-Riser-CL3P-Cable-ACRC.pdf | Composite Fiber/Copper
ACRC004-003X12AWG | 0.412 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-Riser-CL3P-Cable-ACRC.pdf | Composite Fiber/Copper
ACRC004-004X12AWG | 0.48 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-Riser-CL3P-Cable-ACRC.pdf | Composite Fiber/Copper
ACRC006-002X12AWG | 0.375 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-Riser-CL3P-Cable-ACRC.pdf | Composite Fiber/Copper
ACRC008-004X12AWG | 0.375 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-Riser-CL3P-Cable-ACRC.pdf | Composite Fiber/Copper
ACRC008-004X12AWG | 0.48 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-Riser-CL3P-Cable-ACRC.pdf | Composite Fiber/Copper
ACRC012-002X12AWG | 0.375 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-Riser-CL3P-Cable-ACRC.pdf | Composite Fiber/Copper
ACRC012-003X12AWG | 0.43 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-Riser-CL3P-Cable-ACRC.pdf | Composite Fiber/Copper
ACRC012-004X12AWG | 0.48 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-Riser-CL3P-Cable-ACRC.pdf | Composite Fiber/Copper
ACRC012-006X12AWG | 0.53 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-Riser-CL3P-Cable-ACRC.pdf | Composite Fiber/Copper
|  |  | Composite Fiber/Copper | Dividers are a formula to ensure they show up as an empty space
HDRCK002-002X12AWG | 0.78 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-Riser-CL3R-Cable-Armortek-HDRCK.pdf | Composite Fiber/Copper
HDRCK002-004X12AWG | 0.824 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-Riser-CL3R-Cable-Armortek-HDRCK.pdf | Composite Fiber/Copper
HDRCK002-008X12AWG | 0.824 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Indoor-Outdoor-Riser-CL3R-Cable-Armortek-HDRCK.pdf | Composite Fiber/Copper
ACRCK004-002X12AWG | 0.78 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-Riser-CL3P-Cable-Armortek-ACRCK.pdf | Composite Fiber/Copper
ACRCK004-004X12AWG | 0.901 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-Riser-CL3P-Cable-Armortek-ACRCK.pdf | Composite Fiber/Copper
ACRCK006-002X12AWG | 0.78 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-Riser-CL3P-Cable-Armortek-ACRCK.pdf | Composite Fiber/Copper
ACRCK008-004X12AWG | 0.901 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-Riser-CL3P-Cable-Armortek-ACRCK.pdf | Composite Fiber/Copper
ACRCK012-002X12AWG | 0.78 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-Riser-CL3P-Cable-Armortek-ACRCK.pdf | Composite Fiber/Copper
ACRCK012-004X12AWG | 0.901 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-Riser-CL3P-Cable-Armortek-ACRCK.pdf | Composite Fiber/Copper
ACRCK012-006X12AWG | 0.901 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-Riser-CL3P-Cable-Armortek-ACRCK.pdf | Composite Fiber/Copper
ACRCK012-008X12AWG | 1.001 | https://leviton.com/content/dam/leviton/network-solutions/product_documents/product_specification/Leviton-Spec-Indoor-Outdoor-Riser-CL3P-Cable-Armortek-ACRCK.pdf | Composite Fiber/Copper
|  |  | Composite Fiber/Copper | Dividers are a formula to ensure they show up as an empty space
BHCR02E02D44FFNNPzzzz | 0.37 | https://leviton.com/content/dam/leviton/network-solutions/network-channel-extenders/Leviton-Spec-OneReach-1-Port-MM-Riser-Assembly-BHCR02E02D44FFNNPzzzz.pdf | Composite Fiber/Copper
BHCP02E02D44FFNNPzzzz | 0.34 | https://leviton.com/content/dam/leviton/network-solutions/network-channel-extenders/Leviton-Spec-OneReach-1-Port-MM-Plenum-Assembly-BHCP02E02D44FFNNPzzzz.pdf | Composite Fiber/Copper
BHCR02A02D44FFNNPzzzz | 0.34 | https://leviton.com/content/dam/leviton/network-solutions/network-channel-extenders/Leviton-Spec-OneReach-1-Port-SM-Riser-Assembly-BHCR02A02D44FFNNPzzzz.pdf | Composite Fiber/Copper
BHCP02A02D44FFNNPzzzz | 0.314 | https://leviton.com/content/dam/leviton/network-solutions/network-channel-extenders/Leviton-Spec-OneReach-1-Port-SM-Plenum-Assembly-BHCP02A02D44FFNNPzzzz.pdf | Composite Fiber/Copper
BACR04E02D44FFNNPzzzz | 0.38 | https://leviton.com/content/dam/leviton/network-solutions/network-channel-extenders/Leviton-Spec-OneReach-2-Port-MM-Riser-Assembly-BACR04E02D44FFNNPzzzz.pdf | Composite Fiber/Copper
BACP04E02D44FFNNPzzzz | 0.328 | https://leviton.com/content/dam/leviton/network-solutions/network-channel-extenders/Leviton-Spec-OneReach-2-Port-MM-Plenum-Assembly-BACP04E02D44FFNNPzzzz.pdf | Composite Fiber/Copper
BACR04A02D44FFNNPzzzz | 0.38 | https://leviton.com/content/dam/leviton/network-solutions/network-channel-extenders/Leviton-Spec-OneReach-2-Port-SM-Riser-Assembly-BACR04A02D44FFNNPzzzz.pdf | Composite Fiber/Copper
BACP04A02D44FFNNPzzzz | 0.328 | https://leviton.com/content/dam/leviton/network-solutions/network-channel-extenders/Leviton-Spec-OneReach-2-Port-SM-Plenum-Assembly-BACP04A02D44FFNNPzzzz.pdf | Composite Fiber/Copper
BACR08E04D44FFNNPzzzz | 0.48 | https://leviton.com/content/dam/leviton/network-solutions/network-channel-extenders/Leviton-Spec-OneReach-4-Port-MM-Riser-Assembly-BACR08E04D44FFNNPzzzz.pdf | Composite Fiber/Copper
BACP08E04D44FFNNPzzzz | 0.393 |  | Composite Fiber/Copper
BACR08A04D44FFNNPzzzz | 0.48 | https://leviton.com/content/dam/leviton/network-solutions/network-channel-extenders/Leviton-Spec-OneReach-4-Port-SM-Riser-Assembly-BACR08A04D44FFNNPzzzz.pdf | Composite Fiber/Copper
BACP08A04D44FFNNPzzzz | 0.393 | https://leviton.com/content/dam/leviton/network-solutions/network-channel-extenders/Leviton-Spec-OneReach-4-Port-SM-Plenum-Assembly-BACP08A04D44FFNNPzzzz.pdf | Composite Fiber/Copper
BACR12E02D77NNNNPzzzz | 0.38 |  | Composite Fiber/Copper
BACP12E02D77NNNNPzzzz | 0.317 |  | Composite Fiber/Copper
|  |  | Composite Fiber/Copper | Dividers are a formula to ensure they show up as an empty space
BHKR02E02D44FFNNPzzzz | 0.78 |  | Composite Fiber/Copper
BHKP02E02D44FFNNPzzzz | 0.67 |  | Composite Fiber/Copper
BHKR02A02D44FFNNPzzzz | 0.78 |  | Composite Fiber/Copper
BHKP02A02D44FFNNPzzzz | 0.67 |  | Composite Fiber/Copper
BAKR04E02D44FFNNPzzzz | 0.78 |  | Composite Fiber/Copper
BAKP04E02D44FFNNPzzzz | 0.67 |  | Composite Fiber/Copper
BAKR04A02D44FFNNPzzzz | 0.78 |  | Composite Fiber/Copper
BAKP04A02D44FFNNPzzzz | 0.67 |  | Composite Fiber/Copper
BAKR08E04D44FFNNPzzzz | 0.901 |  | Composite Fiber/Copper
BAKP08E04D44FFNNPzzzz | 0.72 |  | Composite Fiber/Copper
BAKR08A04D44FFNNPzzzz | 0.901 |  | Composite Fiber/Copper
BAKP08A04D44FFNNPzzzz | 0.72 |  | Composite Fiber/Copper
BAKR12E02D77NNNNPzzzz | 0.78 |  | Composite Fiber/Copper
BAKP12E02D77NNNNPzzzz | 0.72 |  | Composite Fiber/Copper
Dividers are a formula to ensure they show up as an empty space
LANMARK™-A689 | 0.265 | https://leviton.com/content/dam/leviton/network-solutions/solutions/docs/Leviton-LANMARK-A689-Cat-6-Solid-CMR-CMX-Outdoor-PVC.pdf | Industrial Ethernet | <--Add new cells here to include them in the drop down
LANMARK™-A750 | 0.313 | https://leviton.com/content/dam/leviton/network-solutions/solutions/docs/Leviton-LANMARK-A750-Cat-6A-XTP-Solid-CMR-CMX-Outdoor-PVC.pdf | Industrial Ethernet
LANMARK™-A753 | 0.238 | https://leviton.com/content/dam/leviton/network-solutions/solutions/docs/Leviton-LANMARK-A753-Cat-5e-Solid-CMR-CMX-Outdoor-PVC.pdf | Industrial Ethernet
LANMARK™-A774 | 0.24 | https://leviton.com/content/dam/leviton/network-solutions/solutions/docs/Leviton-LANMARK-A774-Cat-5e-Solid-TPE.pdf | Industrial Ethernet
LANMARK™-A920 | 0.313 | https://leviton.com/content/dam/leviton/network-solutions/solutions/docs/Leviton-LANMARK-A920-Cat-6A-XTP-Solid-CMR-CMX-Outdoor-PVC.pdf | Industrial Ethernet
LANMARK™-A921 | 0.238 | https://leviton.com/content/dam/leviton/network-solutions/solutions/docs/Leviton-LANMARK-A921-Cat-5e-Solid-CMR-CMX-Outdoor-PVC.pdf | Industrial Ethernet
LANMARK™-A922 | 0.265 | https://leviton.com/content/dam/leviton/network-solutions/solutions/docs/Leviton-LANMARK-A922-Cat-6-Solid-CMR-CMX-Outdoor-PVC.pdf | Industrial Ethernet
|  |  | Industrial Ethernet | Dividers are a formula to ensure they show up as an empty space
LANMARK™-B535 | 0.24 | https://leviton.com/content/dam/leviton/network-solutions/solutions/docs/Leviton-LANMARK-B535-Cat-5e-Solid-2-Pr-TPE.pdf | Industrial Ethernet
LANMARK™-B536 | 0.27 | https://leviton.com/content/dam/leviton/network-solutions/solutions/docs/Leviton-LANMARK-B536-Cat-5e-Solid-2-Pr-Shielded-TPE.pdf | Industrial Ethernet
LANMARK™-B537 | 0.29 | https://leviton.com/content/dam/leviton/network-solutions/solutions/docs/Leviton-LANMARK-B537-Cat-5e-Solid-Shielded-TPE.pdf | Industrial Ethernet
LANMARK™-B540 | 0.25 | https://leviton.com/content/dam/leviton/network-solutions/solutions/docs/Leviton-LANMARK-B540-Cat-5e-PVC.pdf | Industrial Ethernet
LANMARK™-B585 | 0.24 | https://leviton.com/content/dam/leviton/network-solutions/solutions/docs/Leviton-LANMARK-B585-Cat-5e-2-Pr-PVC.pdf | Industrial Ethernet
LANMARK™-B587 | 0.26 | https://leviton.com/content/dam/leviton/network-solutions/solutions/docs/Leviton-LANMARK-B587-Cat-5e-2-Pr-Shielded-PVC.pdf | Industrial Ethernet
LANMARK™-B751 | 0.315 | https://leviton.com/content/dam/leviton/network-solutions/solutions/docs/Leviton-LANMARK-B751-Cat-6A-FTP-Solid-CMR-CMX-Outdoor-PVC.pdf | Industrial Ethernet
LANMARK™-B752 | 0.315 | https://leviton.com/content/dam/leviton/network-solutions/solutions/docs/Leviton-LANMARK-B752-Cat-6-FTP-Solid-CMR-CMX-Outdoor-PVC.pdf | Industrial Ethernet
LANMARK™-B789 | 0.305 | https://leviton.com/content/dam/leviton/network-solutions/solutions/docs/Leviton-LANMARK-B789-Cat-5e-Profinet-Solid-2-Pr-Shielded-TPE.pdf | Industrial Ethernet
LANMARK™-B840 | 0.368 | https://leviton.com/content/dam/leviton/network-solutions/solutions/docs/Leviton-LANMARK-B840-Cat-6-PLTC-FTP-Solid-CMR-CMX-Outdoor-PVC.pdf | Industrial Ethernet
LANMARK™-B907 | 0.3 | https://leviton.com/content/dam/leviton/network-solutions/solutions/docs/Leviton-LANMARK-B907-Cat-5e-Shielded-PVC.pdf | Industrial Ethernet
LANMARK™-B917 | 0.315 | https://leviton.com/content/dam/leviton/network-solutions/solutions/docs/Leviton-LANMARK-B917-Cat-6-FTP-Solid-CMR-CMX-Outdoor-PVC.pdf | Industrial Ethernet
LANMARK™-B919 | 0.315 | https://leviton.com/content/dam/leviton/network-solutions/solutions/docs/Leviton-LANMARK-B919-Cat-6A-FTP-Solid-CMR-CMX-Outdoor-PVC.pdf | Industrial Ethernet
|  |  | Industrial Ethernet | Dividers are a formula to ensure they show up as an empty space
LANMARK™-C538 | 0.24 | https://leviton.com/content/dam/leviton/network-solutions/solutions/docs/Leviton-LANMARK-C538-Cat-5e-High-Flex-2-Pr-TPE.pdf | Industrial Ethernet
LANMARK™-C539 | 0.25 | https://leviton.com/content/dam/leviton/network-solutions/solutions/docs/Leviton-LANMARK-C539-Cat-5e-High-Flex-TPE.pdf | Industrial Ethernet
LANMARK™-C541 | 0.26 | https://leviton.com/content/dam/leviton/network-solutions/solutions/docs/Leviton-LANMARK-C541-Cat-5e-High-Flex-2-Pr-Shielded-TPE.pdf | Industrial Ethernet
LANMARK™-C542 | 0.3 | https://leviton.com/content/dam/leviton/network-solutions/solutions/docs/Leviton-LANMARK-C542-Cat-5e-High-Flex-Shielded-TPE.pdf | Industrial Ethernet
LANMARK™-C545 | 0.322 | https://leviton.com/content/dam/leviton/network-solutions/solutions/docs/Leviton-LANMARK-C545-Cat-6A-24AWG-High-Flex-Shielded-TPE.pdf | Industrial Ethernet
LANMARK™-C547 | 0.31 | https://leviton.com/content/dam/leviton/network-solutions/solutions/docs/Leviton-LANMARK-C547-Cat-5e-Profinet-High-Flex-2-Pr-Shielded-TPE.pdf | Industrial Ethernet
LANMARK™-C637 | 0.29 | https://leviton.com/content/dam/leviton/network-solutions/solutions/docs/Leviton-LANMARK-C637-Cat-6A-26AWG-High-Flex-Shielded-TPE.pdf | Industrial Ethernet
LANMARK™-C773 | 0.224 |  | Industrial Ethernet
LANMARK™-C826 | 0.31 | https://leviton.com/content/dam/leviton/network-solutions/solutions/docs/Leviton-LANMARK-C826-Cat-5e-PLTC-High-Flex-2-Pr-Shielded-TPE.pdf | Industrial Ethernet
LANMARK™-C851 | 0.31 | https://leviton.com/content/dam/leviton/network-solutions/solutions/docs/Leviton-LANMARK-C851-Cat-5e-PLTC-High-Flex-2-Pr-Shielded-TPE.pdf | Industrial Ethernet | <--Drop down options end here